## Exec Summary
DMT Stormwater Resilience - Exec Summary
Region | Al Dhafra
Configurable deadline
| Deadline_Date >> | 2027-02-14
Region Overview
Overview & Criticality
Metric | Count | % of total
Total stormwater hotspots | 155
Very high | 8 | 5.161%
High | 62 | 40%
Medium | 50 | 32.26%
Low | 35 | 22.58%
Highly critical (Very High + High) | 70 | 45.16%
Critical (Medium + Low) | 85 | 54.84%
Coverage (who owns the hotspot area)
Coverage | Count | % of total
Covered by Municipality (developer blank/No) | #REF! | #REF!
Covered by Private Entities / Developers | #REF! | #REF!
Root cause
Root cause | Count | % of total
Topography & Road Engineering | #REF! | #REF!
Inadequate Design Capacity | #REF! | #REF!
Absence of Drainage Network | #REF! | #REF!
Unmapped / CHECK | #REF! | #REF!
Other Metrics
Metric | Count
On existing stormwater network (Yes) | 120
Not on network (No) | 35
Duplicate Hotspot IDs (should be 0) | 0
ADM/IDD pond-scope overlaps flagged | 0
Municipality Emergency Response Plan
Emergency Response - Daily Rate
Metric | Highly Critical | Critical | Total
Hotspots covered | 70 | 85 | 155
Manpower (headcount) | 394 | 194 | 588
Diesel pumps (qty) | 61 | 38 | 99
Combination tankers (qty) | 134 | 58 | 192
Manpower budget (AED) | 118200 | 58200 | 176400
Pumps budget (AED) | 152500 | 95000 | 247500
Tankers budget (AED) | 938000 | 406000 | 1344000
Emergency Budget Daily Rate (AED) | 1208700 | 559200 | 1767900
Total Emergency Response Budget (12 Active Days)
Metric | Highly Critical | Critical | Total
Manpower budget (AED) | 1418400 | 698400 | 2116800
Pumps budget (AED) | 1830000 | 1140000 | 2970000
Tankers budget (AED) | 11256000 | 4872000 | 16128000
Total Emergency Response Budget (AED) | 14504400 | 6710400 | 21214800

## Analysis
[11 empty] | Municipality Emergency Response Plan A For storm events up to a 1-in-10-year event: Very high Criticality hotspot: <2h ¦ High criticality hotspot: <4h ¦ Medium criticality hotspot: <10h ¦ Low criticality hotspot: >10h | [20 empty] | Municipality Emergency Response Plan B For storm events exceeding a 1-in-10-year event: Very high Criticality hotspot: <4h ¦ High criticality hotspot: <6h ¦ Medium criticality hotspot: <10h ¦ Low criticality hotspot: >10h | [5 empty] | IDD Intervention Plan
[38 empty] | Select Yes or No | Select one: Critical Infrastructure, Detailed Design, Fast-Track, or Quick Win | Provide the primary solution such as inlet, pipe, Upgrade to Catchment , Pond / Spillway, etc | Select one: Permanent, Interim, or Temporary | Please specify if additional budget is required for this hotspot (Yes/No) | Provide the requested budget for each applicable hotspot. If a single project spans multiple hotspots, list the budget only once under the primary hotspot. For all other covered hotspot entries, replace the budget with: "Included in Hotspot #X budget." | Provide the current rainfall design event, including the return period | Provide the existing network’s technical or hydraulic capacit | Provide the future or target rainfall design event, including the return period | Provide the future or target network capacity after the planned intervention | Provide the estimated floodwater volume managed by network after intervention | Provide the expected number of hours required for floodwater to recede after intervention | Revise the planned mobilization date | Revise the planned completion date | Select one: Contractor Design phase, Parsons Verification Phase, IDAS Review Phase, Municipality Permitting Phase, Implementation phase, Hand Over Phase | Select Yes or No. Enter Yes only after formal approval has been issued. | Provide the actual mobilization date (only after actual mobilization) | Provide the actual completion date (only after actual completion) | Select one: Not Started, On Track, Delayed, or Completed | Provide the full name of the accountable IDD owner.
Hotspot_ID | Hotspot_Area | Hotspot_Location | Latitude | Longitude | Criticality | Developer_Private_Area | Developer Name | Network_Available | Root_Cause | Root_Cause_Details | Manpower_Qty | Manpower Active-duty AED | Manpower Standby AED | Total Manpower_Budget_AED | Pumps_Qty | Diesel Pump 12 inch Qty | Diesel Pump 8 inch Qty | Diesel Pump 6 inch Qty | Diesel Pump 12 inch AED/Day | Diesel Pump 8 inch AED/Day | Diesel Pump 6 inch AED/Day | Total Pump Daily Rate | Total Pump Active Duty AED2 | Total Pump Standby AED | Pumps_Budget_AED | Tankers_Qty | Tankers_Budget_AED | Concrete_Barrier_AED | Sand_Barrier_AED | Detention_Ponds_AED | Collection_Chamber_AED | Manpower_Qty2 | Manpower_Budget_AED3 | Pumps_Qty4 | Pumps_Budget_AED5 | Tankers_Qty6 | Tankers_Budget_AED7 | IDD Interventoin Planned | IDD_Design_Category | Design Solution | Type of Intervention | Additional Budget Requirment | Additional Budget Requested | Hotspot Network Rain Design Event (Current) | Hotspot Network Design Technical Capacity (Current) | Hotspot Network Rain Design Event (Future) | Hotspot Network Design Technical Capacity (Future) | Flood Volume Capacity after Intervention | Associated recovery time after intervention | Planned_IDD_Mobilization_Date | Planned_IDD_Completion_Date | Project Stage | Approval from IDAS secured (Yes/No) | Actual_Mobilization_Date | Actual_Completion_Date | Intervention status | IDD_Owner_Name | Project | Consultant | Notes
1 | Al Mirfa City | Ar Ra-Fah St | 24.0491 | 53.4656 | High | No |  | Yes | Inadequate design capacity | location of this hotspot is slope area not avaliable in storm water net work, water remove from tanker and dewater pump | 12 |  |  | 3600 | 2 | [9 empty] | 5000 | 2 | 14000 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
2 | Al Mirfa City | AL Mitaynah St | 24.0883 | 53.4816 | Medium | No |  | Yes | Inadequate design capacity | Due to the Level difference of existing area water is acccumulating .Need an Additional chamber with network and to be connected to the newly constructed existing network can solve this issue | 4 |  |  | 1200 | 0 | [9 empty] | 0 | 1 | 7000 | [10 empty] | NO | As Per Coordinates the point is located inside the Plot Limits | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | 0 | N/A | N/A | N/A | N/A |  |  | N/A | N/A |  |  | Emirates Driving School
3 | Al Mirfa City | Obaid Bin Jadaas Al Rumaithi St | 24.0882 | 53.4813 | Medium | No |  | Yes | Inadequate design capacity | Due to the Level difference of existing area water is acccumulating. Pipe line not connected to net work. Garden round about surrounding area | 2 |  |  | 600 | 1 | [9 empty] | 2500 | 0 | 0 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
4 | Al Mirfa City | AL Mitaynah St | 24.0888 | 53.4813 | Medium | No |  | Yes | Inadequate design capacity | Due to the Level difference of existing area water is acccumulating .Need an Additional chamber with network and to be connected to the newly constructed existing network can solve this issue | 2 |  |  | 600 | 1 | [9 empty] | 2500 | 0 | 0 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
5 | Al Mirfa City | Hadbat Al Alam St | 24.101 | 53.4965 | Medium | Yes |  | Yes | Inadequate design capacity | Due to the Level difference of existing area water is acccumulating .Need an Additional chamber with network and to be connected to the newly constructed existing network can solve this issue | 4 |  |  | 1200 | 0 | [9 empty] | 0 | 2 | 14000 | [10 empty] | NO | AS Per Coordinates point is located in Entrance of Yasser Alkhaja Private Commercial Compound | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | N/A | N/A
6 | Al Mirfa City | Al Mughira St | 24.1006 | 53.4821 | Low | No |  | Yes | Inadequate design capacity | This road area in not prober slope | 2 |  |  | 600 | 1 | [9 empty] | 2500 | 0 | 0 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
7 | Al Mirfa City | Al shaheed Ahmed Khamis Al Hammadi St | 24.095 | 53.4818 | Medium | No |  | Yes | Inadequate design capacity | Due to the Level difference of existing area water is acccumulating .Need an Additional chamber with network and to be connected to the newly constructed existing network can solve this issue | 4 |  |  | 1200 | 2 | [9 empty] | 5000 | 0 | 0 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
8 | Al Mirfa City | Al Mughira St | 24.1008 | 53.4857 | Low | No |  | Yes | Inadequate design capacity | Problem is salved | 2 |  |  | 600 | 0 | [9 empty] | 0 | 1 | 7000 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
9 | Al Mirfa City | Bandar Al Marfa ST | 24.0923 | 53.4919 | Medium | No |  | Yes | Inadequate design capacity | Need an Additional chamber with network and to be connected to the newly constructed existing network can solve this issue | 2 |  |  | 600 | 0 | [9 empty] | 0 | 1 | 7000 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
10 | Al Mirfa City | Ad Danah St | 24.0865 | 53.5067 | Medium | No |  | Yes | Inadequate design capacity | Need an Additional chamber with network and to be connected to the newly constructed existing network can solve this issue | 2 |  |  | 600 | 0 | [9 empty] | 0 | 1 | 7000 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
11 | Al Mirfa City | Um Al Amadat St | 24.0588 | 53.4635 | Medium | No |  | Yes | Inadequate design capacity | Water is accumulating due to pipe line is small | 6 |  |  | 1800 | 1 | [9 empty] | 2500 | 2 | 14000 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
12 | Al Mirfa City | Al Mughira St | 24.1006 | 53.4896 | Medium | No |  | Yes | Inadequate design capacity | Problem is salved | 2 |  |  | 600 | 0 | [9 empty] | 0 | 1 | 7000 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
13 | Al Mirfa City | Al Mughira St | 24.0983 | 53.4938 | Medium | No |  | Yes | Inadequate design capacity | Due to the Level difference of existing area water is acccumulating .Need an Additional chamber with network and to be connected to the newly constructed existing network can solve this issue | 4 |  |  | 1200 | 0 | [9 empty] | 0 | 2 | 14000 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
14 | Al Mirfa City | Al Mughira St | 24.0988 | 53.4928 | Medium | No |  | Yes | Inadequate design capacity | Due to the Level difference of existing area water is acccumulating .Need an Additional chamber with network and to be connected to the newly constructed existing network can solve this issue | 2 |  |  | 600 | 0 | [9 empty] | 0 | 1 | 7000 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
15 | Al Mirfa City | Al Mughira St | 24.0984 | 53.4943 | Medium | No |  | Yes | Inadequate design capacity | Due to the Level difference of existing area water is acccumulating .Need an Additional chamber with network and to be connected to the newly constructed existing network can solve this issue | 2 |  |  | 600 | 0 | [9 empty] | 0 | 1 | 7000 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
16 | Al Mirfa City | Al Mughira St | 24.098 | 53.4942 | Medium | No |  | Yes | Inadequate design capacity | Due to the Level difference of existing area water is acccumulating .Need an Additional chamber with network and to be connected to the newly constructed existing network can solve this issue | 4 |  |  | 1200 | 0 | [9 empty] | 0 | 2 | 14000 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
17 | Al Mirfa City | Al Mughira St | 24.0865 | 53.5146 | Low | No |  | Yes | Inadequate design capacity | outer area level is higher than the pipe level, remove the water with heavy diesel engine to the near open sand area | 2 |  |  | 600 | 1 | [9 empty] | 2500 | 0 | 0 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
18 | Al Mirfa City | Al Mughira St | 24.0711 | 53.5441 | Medium | No |  | Yes | Inadequate design capacity | outer area level is higher than the pipe level, remove the water with heavy diesel engine to the near open sand area | 2 |  |  | 600 | 1 | [9 empty] | 2500 | 0 | 0 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A |  |  | Entrance of Smart Impound Parking Area
19 | Al Mirfa City | Tarif area | 24.0084 | 53.7284 | Medium | No |  | Yes | Inadequate design capacity | Need to install collection chamber | 4 |  |  | 1200 | 1 | [9 empty] | 2500 | 1 | 7000 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A |  |  | Alzafra Cooperative Society
20 | Al Mirfa City | In front of the ADCO | 24.0886 | 53.4791 | Medium | No |  | Yes | Inadequate design capacity | Due to the Level difference of existing area water is acccumulating .Need an Additional chamber with network and to be connected to the newly constructed existing network can solve this issue | 4 |  |  | 1200 | 1 | [9 empty] | 2500 | 1 | 7000 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
21 | Al Mirfa City | Al Mirfa Port | 24.0995 | 53.4936 | Medium | No |  | Yes | Inadequate design capacity | Due to the Level difference of existing area water is acccumulating .Need an Additional chamber with network and to be connected to the newly constructed existing network can solve this issue | 2 |  |  | 600 | 1 | [9 empty] | 2500 | 0 | 0 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
22 | Al Mirfa City | Al shaheed Ahmed Khamis Al Hammadi St | 24.0762 | 53.4745 | Medium | No |  | Yes | Inadequate design capacity | Due to the Level difference of existing area water is acccumulating .Need an Additional chamber with network and to be connected to the newly constructed existing network can solve this issue | 2 |  |  | 600 | 0 | [9 empty] | 0 | 1 | 7000 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
23 | Al Mirfa City | Al shaheed Ahmed Khamis Al Hammadi St | 24.0719 | 53.4726 | Medium | No |  | Yes | Inadequate design capacity | Due to the Level difference of existing area water is acccumulating .Need an Additional chamber with network and to be connected to the newly constructed existing network can solve this issue | 2 |  |  | 600 | 0 | [9 empty] | 0 | 1 | 7000 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
24 | Al Mirfa City | Al shaheed Ahmed Khamis Al Hammadi St | 24.0884 | 53.4801 | Medium | No |  | Yes | Inadequate design capacity | Due to the Level difference of existing area water is acccumulating. | 2 |  |  | 600 | 0 | [9 empty] | 0 | 1 | 7000 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
25 | Al Mirfa City | Obaid Bin Jadaas Al Rumaithi St | 24.0875 | 53.4814 | Medium | No |  | Yes | Inadequate design capacity | Due to the Level difference of existing area water is acccumulating. | 2 |  |  | 600 | 0 | [9 empty] | 0 | 1 | 7000 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A |  |  | Mirfa Bus Station Entrance
26 | Al Mirfa City | Jazeerat Salahah St | 24.087 | 53.4807 | Medium | No |  | Yes | Inadequate design capacity | Due to the Level difference of existing area water is acccumulating. | 2 |  |  | 600 | 1 | [9 empty] | 2500 | 0 | 0 | [10 empty] | NO | Same area as HS# 25 , Work Order Should be one | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
27 | Al Mirfa City | Obaid Bin Jadaas Al Rumaithi St | 24.0875 | 53.4818 | Medium | No |  | Yes | Inadequate design capacity | Due to the Level difference of existing area water is acccumulating. | 2 |  |  | 600 | 1 | [9 empty] | 2500 | 0 | 0 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A |  |  | Mirfa Bus Station Customer Parking
28 | Al Mirfa City | Obaid Bin Jadaas Al Rumaithi St | 24.087 | 53.4837 | Medium | No |  | Yes | Inadequate design capacity | Due to the Level difference of existing area water is acccumulating .Need an Additional chamber with network and to be connected to the newly constructed existing network can solve this issue | 4 |  |  | 1200 | 1 | [9 empty] | 2500 | 1 | 7000 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
29 | Al Mirfa City | Qussar Al Madfar St | 24.0903 | 53.5001 | Medium | No |  | Yes | Inadequate design capacity | Due to the Level difference of existing area water is acccumulating .Need an Additional chamber with network and to be connected to the newly constructed existing network can solve this issue | 2 |  |  | 600 | 1 | [9 empty] | 2500 | 0 | 0 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
30 | Al Sila' | Al Sila Street | 24.0841 | 51.7643 | Low | No |  | No | Absence of drainage network | location of this hotspot is parking area inside park and if the slop of the parking ground is adjusted towerds the corner of the ground the accumulated water will get space to flow to the road and flow towers adjacent storm chamber. | 4 |  |  | 1200 | 2 | [9 empty] | 5000 | 0 | 0 | [10 empty] | Yes | Detailed Design | Stormwater Network including pipes, inlets and manholes | Permanent | no | 0 | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | N/A | N/A | 2024-07-01 | 2026-01-01 | Project Closeout and Handover | Yes | 2024-07-01 | 2026-01-01 | Completed | DMT Project Manager | Silaa Stormwater Phase 2 DRM | KN | Al Shabhana Park External Parking
31 | Al Sila' | Al Bawakhir Street | 24.0814 | 51.7844 | High | No |  | No | Absence of drainage network | Due to the fluctuation of the road level water is accumulating and totally obstructing the movement of vehicles .Better to transfer these water towerds near sea or to the sandy area with Booster engine | 4 |  |  | 1200 | 2 | [9 empty] | 5000 | 0 | 0 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
32 | Al Sila' | Al Sila Street | 24.0841 | 51.7643 | Low | No |  | No | Absence of drainage network | location of this hotspot is parking area inside park and if the slop of the parking ground is adjusted towerds the corner of the ground the accumulated water will get space to flow to the road and flow towers adjacent storm chamber. | 4 |  |  | 1200 | 2 | [9 empty] | 5000 | 0 | 0 | [10 empty] | Yes | Detailed Design | Stormwater Network including pipes, inlets and manholes | Permanent | no | 0 | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | N/A | N/A | 2022-11-01 | 2026-01-01 | Project Closeout and Handover | Yes | 2024-07-01 | 2026-01-01 | Completed | DMT Project Manager | Silaa Infill Plots - Aldar | KN | Al Shabhana Park External Parking
33 | Al Sila' | Al Mina Street | 24.078 | 51.7579 | Low | No |  | No | Absence of drainage network | Water is accumulating the back entrace of the school and the level of ground is lower than the near available network chamber.Additional chamber with network line is the better and permenent solution. | 2 |  |  | 600 | 0 | [9 empty] | 0 | 1 | 7000 | [10 empty] | Yes | Detailed Design | Stormwater Network including pipes, inlets and manholes | Permanent | no | 0 | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | N/A | N/A | 2024-07-01 | 2026-01-01 | Project Closeout and Handover | Yes | 2024-07-01 | 2026-01-01 | Completed | DMT Project Manager | Silaa Stormwater Phase 2 DRM | KN
34 | Al Sila' | Al Qirdiyyah Street | 24.066 | 51.7521 | High | No |  | No | Absence of drainage network | Water is accumulating in front of the residence parking area .Need additional chmber with network connection and to connected to the near existing network can solve this issue. (Opposite road network with chamber available) | 6 |  |  | 1800 | 2 | [9 empty] | 5000 | 1 | 7000 | [10 empty] | Yes | Detailed Design | Stormwater Network including pipes, inlets and manholes | Permanent | no | 0 | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | N/A | N/A | 2024-07-01 | 2026-01-01 | Project Closeout and Handover | Yes | 2024-07-01 | 2026-01-01 | Completed | DMT Project Manager | Silaa Stormwater Phase 2 DRM | KN
35 | Al Sila' | Al Rai Street | 24.0699 | 51.7664 | High | No |  | No | Absence of drainage network | Due to the level variation of existing road, water is accumulating and obstructing the movement of vehicles.Need additional chamber with network connection and connected to the very near existing chamber. | 6 |  |  | 1800 | 2 | [9 empty] | 5000 | 1 | 7000 | [10 empty] | Yes | Detailed Design | Stormwater Network including pipes, inlets and manholes | Permanent | no | 0 | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | N/A | N/A | 2022-11-01 | 2026-01-01 | Project Closeout and Handover | Yes | 2024-07-01 | 2026-01-01 | Completed | DMT Project Manager | Silaa Infill Plots - Aldar | KN
36 | Al Sila' | Al Mina Street | 24.0808 | 51.715 | High | No |  | No | Absence of drainage network | Water is accumulating due to the level variation of the area and Need a new network system or remove the water with heavy booster engine to the near open sand area. | 4 |  |  | 1200 | 1 | [9 empty] | 2500 | 1 | 7000 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
37 | Al Sila' | Al Suheel street | 24.0429 | 51.7624 | Low | No |  | No | Absence of drainage network | Due to the Level difference of existing area water is acccumulating .Need an Additional chamber with network and to be connected to the newly constructed existing network can solve this issue (Near road side) | 4 |  |  | 1200 | 1 | [9 empty] | 2500 | 1 | 7000 | [10 empty] | Yes | Detailed Design | Stormwater Network including pipes, inlets and manholes | Permanent | no | 0 | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | N/A | N/A | 2024-07-01 | 2026-01-01 | Project Closeout and Handover | Yes | 2024-07-01 | 2026-01-01 | Completed | DMT Project Manager | Silaa Stormwater Phase 2 DRM | KN
38 | Al Sila' | Al Marouf Street | 24.0769 | 51.7665 | High | No |  | Yes | Inadequate design capacity | Water is accumulating in front of the parking area of ADIB bank and due to the level variation od ground ,failed to flow these water to the nearest existing chamber.Additional network connection to the existing can solve this issue. | 6 |  |  | 1800 | 1 | [9 empty] | 2500 | 2 | 14000 | [10 empty] | Yes | Detailed Design | Stormwater Network including pipes, inlets and manholes | Permanent | no | 0 | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | N/A | N/A | 2022-11-01 | 2026-01-01 | Project Closeout and Handover | Yes | 2024-07-01 | 2026-01-01 | Completed | DMT Project Manager | Silaa Infill Plots - Aldar | KN
39 | Al Sila' | Al Bawakhir Street | 24.0772 | 51.7836 | High | No |  | No | Absence of drainage network | Due to the fluctuation of the road level water is accumulationg and totally disturbing the movement of vehicles .Better to transfer these water towerds near sea with Booster engine | 10 |  |  | 3000 | 2 | [9 empty] | 5000 | 3 | 21000 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
40 | Al Sila' | Shat Al Arab Street | 24.0576 | 51.774 | Low | No |  | No | Absence of drainage network | Due to the level variation of the road water is accumulating and moreover no any network is near in this area. Better to removed the accumulated water by dewatering engine to the near open sandy area.( extrem back road of sila industrial area) | 2 |  |  | 600 | 1 | [9 empty] | 2500 | 0 | 0 | [10 empty] | Yes | Detailed Design | Stormwater Network including pipes, inlets and manholes | Permanent | no | 0 | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | N/A | N/A | 2027-03-01 | 2028-03-01 | Implementation Phase | Yes |  |  | On Track | DMT Project Manager | Silaa Stormwater Phase 3 DRM | KN
41 | Al Sila' | Al Meena Street | 24.0645 | 51.7834 | High | Yes |  | No | Absence of drainage network | Water is accumulating and obstructing the movement of vehicle in inside SILA BEACH FRONT. Due to the poor level variation of parking road water is accumulating.No network availble in these area and better solution is to remove water towerds very near sea are through booster engine. | 6 |  |  | 1800 | 2 | [9 empty] | 5000 | 1 | 7000 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
42 | Al Sila' | Ras Ghumais street | 24.3349 | 51.6076 | High | No |  | No | Absence of drainage network | Need new network system | 6 |  |  | 1800 | 1 | [9 empty] | 2500 | 2 | 14000 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
43 | Madinat Zayed City | Salama Bint Butti road ENTRANCE MADINAT ZAYED | 23.698 | 53.6854 | high | No |  | Yes | Inadequate design capacity | Need new network system | 10 |  |  | 3000 | 1 | [9 empty] | 2500 | 4 | 28000 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
44 | Madinat Zayed City | Entrance Marbee aldhfra | 23.6127 | 53.7104 | high | No |  | Yes | Inadequate design capacity | Need new network system | 10 |  |  | 3000 | 1 | [9 empty] | 2500 | 4 | 28000 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A |  |  | Marbee aldhfra
45 | Madinat Zayed City | Entrance Marbee aldhfra | 23.6081 | 53.7185 | high | No |  | Yes | Inadequate design capacity | Need new network system | 10 |  |  | 3000 | 1 | [9 empty] | 2500 | 4 | 28000 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
46 | Madinat Zayed City | Camel race | 23.5661 | 53.7526 | low | No |  | No | Absence of drainage network | Need new network system | 2 |  |  | 600 | 0 | [9 empty] | 0 | 1 | 7000 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
47 | Madinat Zayed City | Al hadga entrance | 23.624 | 53.7178 | low | No |  | No | Absence of drainage network | Need new network system | 2 |  |  | 600 | [10 empty] | 0 | 1 | 7000 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
48 | Madinat Zayed City | municipality barking | 23.6227 | 53.7166 | low | No |  | No | Absence of drainage network | Need new network system | 2 |  |  | 600 | [10 empty] | 0 | 1 | 7000 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
49 | Madinat Zayed City | Adefsa barking | 23.6243 | 53.7161 | low | Yes |  | No | Absence of drainage network | Need new network system | 2 |  |  | 600 | [10 empty] | 0 | 1 | 7000 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
50 | Madinat Zayed City | Test vehicle round about | 23.6327 | 53.7131 | low | No |  | No | Absence of drainage network | Need new network system | 2 |  |  | 600 | [10 empty] | 0 | 1 | 7000 | [10 empty] | Yes | Detailed Design | Stormwater Network including pipes, inlets and manholes | Permanent | no | 0 | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | N/A | N/A | 2027-03-01 | 2028-03-01 | Implementation Phase | Yes | 2024-07-01 |  | On Track | DMT Project Manager |  | Parsons International
51 | Madinat Zayed City | Salama Bint Butti road | 23.6409 | 53.7104 | very high | No |  | Yes | Inadequate design capacity | Need new network system | 10 |  |  | 3000 | 1 | [9 empty] | 2500 | 4 | 28000 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
52 | Madinat Zayed City | Salama Bint Butti road | 23.6421 | 53.7099 | very high | No |  | Yes | Inadequate design capacity | Need new network system | 10 |  |  | 3000 | 1 | [9 empty] | 2500 | 4 | 28000 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
53 | Madinat Zayed City | Salama Bint Butti road | 23.6467 | 53.7096 | very high | No |  | Yes | Inadequate design capacity | Need new network system | 10 |  |  | 3000 | 1 | [9 empty] | 2500 | 4 | 28000 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
54 | Madinat Zayed City | Salama Bint Butti road | 23.6464 | 53.708 | very high | No |  | Yes | Inadequate design capacity | Need new network system | 10 |  |  | 3000 | 1 | [9 empty] | 2500 | 4 | 28000 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
55 | Madinat Zayed City | Salama Bint Butti road | 23.649 | 53.707 | very high | No |  | Yes | Inadequate design capacity | Need new network system | 10 |  |  | 3000 | 1 | [9 empty] | 2500 | 4 | 28000 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
56 | Madinat Zayed City | Fish market | 23.6499 | 53.704 | low | Yes |  | No | Absence of drainage network | Need new network system | 4 |  |  | 1200 | 1 | [9 empty] | 2500 | 1 | 7000 | [10 empty] | Yes | Detailed Design | Stormwater Network including pipes, inlets and manholes | Permanent | no | 0 | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | N/A | N/A | 2027-03-01 | 2028-03-01 | Implementation Phase | Yes | 2024-07-01 |  | On Track | DMT Project Manager |  | Parsons International
57 | Madinat Zayed City | Mohamed khalaf road | 23.6533 | 53.7016 | high | No |  | No | Absence of drainage network | Need new network system | 4 |  |  | 1200 | 1 | [9 empty] | 2500 | 1 | 7000 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
58 | Madinat Zayed City | Mohamed khalaf road | 23.6534 | 53.6943 | low | No |  | No | Absence of drainage network | Need new network system | 0 |  |  | 0 | [10 empty] | 0 | 0 | 0 | [10 empty] | Yes | Detailed Design | Stormwater Network including pipes, inlets and manholes | Permenent | no | 0 | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | N/A | N/A | TBC | TBC | Future Implementation | Yes |  |  | Not Started | DMT Project Manager |  | Parsons International
59 | Madinat Zayed City | Mohamed khalaf road | 23.6539 | 53.6798 | low | No |  | No | Absence of drainage network | Need new network system | 0 |  |  | 0 | [10 empty] | 0 | 0 | 0 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
60 | Madinat Zayed City | Mohamed khalaf road | 23.6541 | 53.6734 | high | No |  | No | Absence of drainage network | Need new network system | 4 |  |  | 1200 | [10 empty] | 0 | 2 | 14000 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
61 | Madinat Zayed City | New shabia | 23.6491 | 53.6937 | low | No |  | Yes | Inadequate design capacity | Need new network system | 0 |  |  | 0 | [10 empty] | 0 | 0 | 0 | [10 empty] | Yes | Detailed Design | Stormwater Network including pipes, inlets and manholes | Permenent | no | 0 | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | N/A | N/A | TBC | TBC | Future Implementation | Yes |  |  | Not Started | DMT Project Manager |  | Parsons International
62 | Madinat Zayed City | Wedding Hall parking | 23.6527 | 53.682 | low | No |  | Yes | Inadequate design capacity | Need new network system | 0 |  |  | 0 | [10 empty] | 0 | 0 | 0 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
63 | Madinat Zayed City | Salama Bint Butti road | 23.6545 | 53.6951 | low | No |  | Yes | Inadequate design capacity | Need new network system | 0 |  |  | 0 | [10 empty] | 0 | 0 | 0 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
64 | Madinat Zayed City | shabiat al awamer | 23.6545 | 53.6972 | low | No |  | Yes | Inadequate design capacity | Need new network system | 0 |  |  | 0 | [10 empty] | 0 | 0 | 0 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
65 | Madinat Zayed City | shabiat al awamer | 23.6554 | 53.6967 | low | No |  | Yes | Inadequate design capacity | Need new network system | 0 |  |  | 0 | [10 empty] | 0 | 0 | 0 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
66 | Madinat Zayed City | shabiat al awamer | 23.6565 | 53.7024 | low | No |  | Yes | Inadequate design capacity | Need new network system | 0 |  |  | 0 | [10 empty] | 0 | 0 | 0 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
67 | Madinat Zayed City | Salama Bint Butti road | 23.6572 | 53.7033 | high | No |  | Yes | Inadequate design capacity | Need new network system | 10 |  |  | 3000 | 1 | [9 empty] | 2500 | 4 | 28000 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
68 | Madinat Zayed City | inside al dhfra court | 23.6582 | 53.6986 | low | No |  | Yes | Inadequate design capacity | Need new network system | 0 |  |  | 0 | [10 empty] | 0 | 0 | 0 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
69 | Madinat Zayed City | New shabia | 23.6502 | 53.6952 | low | No |  | Yes | Absence of drainage network | Need new network system | 0 |  |  | 0 | [10 empty] | 0 | 0 | 0 | [10 empty] | Yes | Detailed Design | Stormwater Network including pipes, inlets and manholes | Permenent | no | 0 | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | N/A | N/A | TBC | TBC | Future Implementation | Yes |  |  | Not Started | DMT Project Manager |  | Parsons International
70 | Madinat Zayed City | Salama Bint Butti road | 23.6662 | 53.6995 | high | No |  | Yes | Inadequate design capacity | Need new network system | 0 |  |  | 0 | [10 empty] | 0 | 0 | 0 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
71 | Madinat Zayed City | Salama Bint Butti road | 23.6691 | 53.698 | low | No |  | Yes | Inadequate design capacity | Need new network system | 10 |  |  | 3000 | 1 | [9 empty] | 2500 | 4 | 28000 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
72 | Madinat Zayed City | entrance aldhfra club | 23.6684 | 53.6963 | high | No |  | No | Absence of drainage network | Need new network system | 10 |  |  | 3000 | 1 | [9 empty] | 2500 | 4 | 28000 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
73 | Madinat Zayed City | entrance aldhfra club | 23.6679 | 53.695 | high | No |  | No | Absence of drainage network | Need new network system | 10 |  |  | 3000 | 1 | [9 empty] | 2500 | 4 | 28000 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
74 | Madinat Zayed City | Salama Bint Butti road | 23.6801 | 53.6931 | low | No |  | Yes | Inadequate design capacity | Need new network system | 0 |  |  | 0 | [10 empty] | 0 | 0 | 0 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
75 | Madinat Zayed City | Sanaeya madinat zayed | 23.6602 | 53.7259 | high | No |  | No | Absence of drainage network | Need new network system | 10 |  |  | 3000 | 1 | [9 empty] | 2500 | 4 | 28000 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
76 | Madinat Zayed City | old shabia | 23.6555 | 53.7112 | low | No |  | No | Absence of drainage network | Need new network system | 0 |  |  | 0 | [10 empty] | 0 | 0 | 0 | [10 empty] | Yes | Detailed Design | Stormwater Network including pipes, inlets and manholes | Permenent | no | 0 | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | N/A | N/A | TBC | TBC | Future Implementation | Yes |  |  | Not Started | DMT Project Manager |  | Parsons International
77 | Madinat Zayed City | Salama Bint Butti road | 23.6221 | 53.7171 | low | No |  | Yes | Inadequate design capacity | Need new network system | 0 |  |  | 0 | [10 empty] | 0 | 0 | 0 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
78 | Madinat Zayed City | humb area | 23.6459 | 53.7075 | low | No |  | No | Absence of drainage network | Need new network system | 0 |  |  | 0 | [10 empty] | 0 | 0 | 0 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
79 | Madinat Zayed City | Salama Bint Butti road | 23.6577 | 53.7031 | high | No |  | Yes | Inadequate design capacity | Need new network system | 10 |  |  | 3000 | 1 | [9 empty] | 2500 | 4 | 28000 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
80 | Madinat Zayed City | old shabia | 23.6555 | 53.7054 | low | No |  | No | Absence of drainage network | Need new network system | 0 |  |  | 0 | [10 empty] | 0 | 0 | 0 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
81 | Madinat Zayed City | old shabia | 23.6554 | 53.7044 | low | No |  | No | Absence of drainage network | Need new network system | 0 |  |  | 0 | [10 empty] | 0 | 0 | 0 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
82 | Madinat Zayed City | Test vehicle round about | 23.6325 | 53.7134 | low | No |  | No | Absence of drainage network | Need new network system | 0 |  |  | 0 | [10 empty] | 0 | 0 | 0 | [10 empty] | Yes | Detailed Design | Stormwater Network including pipes, inlets and manholes | Permenent | no | 0 | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | N/A | N/A | TBC | TBC | Future Implementation | Yes |  |  | Not Started | DMT Project Manager |  | Parsons International
83 | Madinat Zayed City | Entrance Marbee aldhfra | 23.6082 | 53.7187 | high | No |  | Yes | Inadequate design capacity | Need new network system | 10 |  |  | 3000 | 1 | [9 empty] | 2500 | 4 | 28000 | [10 empty] | NO | Subject to the future Projects Same Area as HS # 45 | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
84 | Madinat Zayed City | Salama Bint Butti road | 23.6189 | 53.7181 | high | No |  | Yes | Inadequate design capacity | Need new network system | 10 |  |  | 3000 | 1 | [9 empty] | 2500 | 4 | 28000 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
85 | Madinat Zayed City | Marbee aldhfra | 23.6057 | 53.7023 | high | No |  | No | Absence of drainage network | Need new network system | 10 |  |  | 3000 | 1 | [9 empty] | 2500 | 4 | 28000 | [10 empty] | YES | Detailed Design | network with Pond outfall | Permenent | No | 0 | 1 in 5 Years, check in 1 in 10 Years | 44.88mm & check on 51.12mm | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | N/A | N/A | TBC | TBC | Future Implementation | Yes |  |  | Not Started | DMT Project Manager |  | Al Torath
86 | Madinat Zayed City | Marbee aldhfra | 23.6065 | 53.7008 | high | No |  | No | Absence of drainage network | Need new network system | 10 |  |  | 3000 | 1 | [9 empty] | 2500 | 4 | 28000 | [10 empty] | YES | Detailed Design | network with Pond outfall | Permenent | No | 0 | 1 in 5 Years, check in 1 in 10 Years | 44.88mm & check on 51.12mm | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | N/A | N/A | TBC | TBC | Future Implementation | Yes |  |  | Not Started | DMT Project Manager |  | Al Torath
87 | Madinat Zayed City | Marbee aldhfra | 23.6082 | 53.7048 | high | No |  | No | Absence of drainage network | Need new network system | 10 |  |  | 3000 | 1 | [9 empty] | 2500 | 4 | 28000 | [10 empty] | YES | Detailed Design | network with Pond outfall | Permenent | No | 0 | 1 in 5 Years, check in 1 in 10 Years | 44.88mm & check on 51.12mm | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | N/A | N/A | TBC | TBC | Future Implementation | Yes |  |  | Not Started | DMT Project Manager |  | Al Torath
88 | Madinat Zayed City | Marbee aldhfra | 23.6046 | 53.7039 | high | No |  | No | Absence of drainage network | Need new network system | 10 |  |  | 3000 | 1 | [9 empty] | 2500 | 4 | 28000 | [10 empty] | YES | Detailed Design | network with Pond outfall | Permenent | No | 0 | 1 in 5 Years, check in 1 in 10 Years | 44.88mm & check on 51.12mm | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | N/A | N/A | TBC | TBC | Future Implementation | Yes |  |  | Not Started | DMT Project Manager |  | Al Torath
89 | Madinat Zayed City | Marbee aldhfra | 23.6097 | 53.7127 | high | No |  | No | Absence of drainage network | Need new network system | 10 |  |  | 3000 | 1 | [9 empty] | 2500 | 4 | 28000 | [10 empty] | YES | Detailed Design | network with Pond outfall | Permenent | No | 0 | 1 in 5 Years, check in 1 in 10 Years | 44.88mm & check on 51.12mm | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | N/A | N/A | TBC | TBC | Future Implementation | Yes |  |  | Not Started | DMT Project Manager |  | Al Torath
90 | Delma City | Al huwad | 24.5015 | 52.3327 | high | No |  | Yes | Inadequate design capacity | Need new network system | 4 |  |  | 1200 | 1 | [9 empty] | 2500 | 1 | 7000 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
91 | Delma City | Al huwad | 24.4928 | 52.3294 | high | No |  | Yes | Topography & Road Engineering | Need new network system | 6 |  |  | 1800 | 1 | [9 empty] | 2500 | 2 | 14000 | [10 empty] | Yes | Detailed Design | Stormwater Network including pipes, inlets and manholes | Permanent | no | 0 | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | N/A | N/A | 2025-06-01 | 2027-03-01 | Project Execution and Monitoring | Yes | 2025-06-01 |  | Not Started | DMT Project Manager | DRM Stormwater Delma-002-23 | KN
92 | Delma City | Al huwad | 24.4842 | 52.3231 | high | No |  | Yes | Topography & Road Engineering | Need new network system | 4 |  |  | 1200 | 1 | [9 empty] | 2500 | 1 | 7000 | [10 empty] | Yes | Detailed Design | Stormwater Network including pipes, inlets and manholes | Permanent | no | 0 | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | N/A | N/A | 2025-06-01 | 2027-03-01 | Project Execution and Monitoring | Yes | 2025-06-01 |  | Not Started | DMT Project Manager | DRM Stormwater Delma-002-23 | KN
93 | Delma City | Bad shayl | 24.4742 | 52.3164 | Medium | No |  | Yes | Inadequate design capacity | Need new network system | 4 |  |  | 1200 | 1 | [9 empty] | 2500 | 1 | 7000 | [10 empty] | Yes | Detailed Design | Stormwater Network including pipes, inlets and manholes | Permanent | no | 0 | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | N/A | N/A | 2025-06-01 | 2027-03-01 | Project Execution and Monitoring | Yes | 2025-06-01 |  | Not Started | DMT Project Manager | DRM Stormwater Delma-002-23 | KN
94 | Delma City | Al huwad | 24.4723 | 52.3161 | high | No |  | Yes | Topography & Road Engineering | Need new network system | 2 |  |  | 600 | 0 | [9 empty] | 0 | 1 | 7000 | [10 empty] | Yes | Detailed Design | Stormwater Network including pipes, inlets and manholes | Permanent | no | 0 | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | N/A | N/A | 2025-06-01 | 2027-03-01 | Project Execution and Monitoring | Yes | 2025-06-01 |  | Not Started | DMT Project Manager | DRM Stormwater Delma-002-23 | KN
95 | Delma City | Bad shayl | 24.4686 | 52.3166 | high | No |  | Yes | Topography & Road Engineering | Need new network system | 2 |  |  | 600 | 1 | [9 empty] | 2500 | 0 | 0 | [10 empty] | Yes | Detailed Design | Stormwater Network including pipes, inlets and manholes | Permanent | no | 0 | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | N/A | N/A | 2025-06-01 | 2027-03-01 | Project Execution and Monitoring | Yes | 2025-06-01 |  | Not Started | DMT Project Manager | DRM Stormwater Delma-002-23 | KN
96 | Delma City | Al huwad | 24.4667 | 52.3165 | high | No |  | Yes | Topography & Road Engineering | Need new network system | 2 |  |  | 600 | [10 empty] | 0 | 1 | 7000 | [10 empty] | Yes | Detailed Design | Stormwater Network including pipes, inlets and manholes | Permanent | no | 0 | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | N/A | N/A | 2025-06-01 | 2027-03-01 | Project Execution and Monitoring | Yes | 2025-06-01 |  | Not Started | DMT Project Manager | DRM Stormwater Delma-002-23 | KN
97 | Delma City | Bad”s-hayl | 24.4728 | 52.3118 | high | No |  | Yes | Topography & Road Engineering | Need new network system | 2 |  |  | 600 | [10 empty] | 0 | 1 | 7000 | [10 empty] | NO | Detailed Design " Point looks as per coordinates is located inside the Mosque Plot Limits " | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | N/A | N/A | DRM Stormwater Delma-002-23 | KN
98 | Delma City | Shk.Zayed Bin Sultan | 24.4857 | 52.3002 | high | No |  | Yes | Topography & Road Engineering | Need new network system | 4 |  |  | 1200 | 1 | [9 empty] | 2500 | 1 | 7000 | [10 empty] | Yes | Detailed Design | Stormwater Network including pipes, inlets and manholes | Permanent | no | 0 | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | N/A | N/A | 2025-06-01 | 2027-03-01 | Project Execution and Monitoring | Yes | 2025-06-01 |  | Not Started | DMT Project Manager | DRM Stormwater Delma-002-23 | KN
99 | Delma City | Al Qusour | 24.4823 | 52.3048 | high | No |  | Yes | Inadequate design capacity | Need new network system | 2 |  |  | 600 | [10 empty] | 0 | 1 | 7000 | [10 empty] | Yes | Detailed Design | Stormwater Network including pipes, inlets and manholes | Permanent | no | 0 | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | N/A | N/A | 2025-06-01 | 2027-03-01 | Project Execution and Monitoring | Yes | 2025-06-01 |  | Not Started | DMT Project Manager | DRM Stormwater Delma-002-23 | KN
100 | Delma City | Shk.Zayed Bin Sultan | 24.4882 | 52.2944 | high | No |  | Yes | Topography & Road Engineering | Need new network system | 2 |  |  | 600 | 1 | [9 empty] | 2500 | 0 | 0 | [10 empty] | Yes | Detailed Design | Stormwater Network including pipes, inlets and manholes | Permanent | no | 0 | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | N/A | N/A | 2025-06-01 | 2027-03-01 | Project Execution and Monitoring | Yes | 2025-06-01 |  | Not Started | DMT Project Manager | DRM Stormwater Delma-002-23 | KN
101 | Delma City | Shk.Zayed Bin Sultan | 24.4857 | 52.3002 | high | No |  | Yes | Topography & Road Engineering | Need new network system | 8 |  |  | 2400 | 2 | [9 empty] | 5000 | 2 | 14000 | [10 empty] | Yes | Detailed Design " same Point as Hot Spot 98" | Stormwater Network including pipes, inlets and manholes | Permanent | no | 0 | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | N/A | N/A | 2025-06-01 | 2027-03-01 | Project Execution and Monitoring | Yes | 2025-06-01 |  | Not Started | DMT Project Manager | DRM Stormwater Delma-002-23 | KN | Shk.Zayed Bin Sultan " same Point as Hot Spot 98"
102 | Delma City | Makka | 24.4905 | 52.3233 | high | No |  | Yes | Inadequate design capacity | Need new network system | 2 |  |  | 600 | [10 empty] | 0 | 1 | 7000 | [10 empty] | Yes | Detailed Design | Stormwater Network including pipes, inlets and manholes | Permanent | no | 0 | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | N/A | N/A | 2025-06-01 | 2027-03-01 | Project Execution and Monitoring | Yes | 2025-06-01 |  | Not Started | DMT Project Manager | DRM Stormwater Delma-002-23 | KN
103 | Delma City | Shk.Zayed Bin Sultan | 24.4887 | 52.3156 | high | No |  | Yes | Topography & Road Engineering | Need new network system | 8 |  |  | 2400 | 2 | [9 empty] | 5000 | 2 | 14000 | [10 empty] | Yes | Detailed Design | Stormwater Network including pipes, inlets and manholes | Permanent | no | 0 | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | N/A | N/A | 2025-06-01 | 2027-03-01 | Project Execution and Monitoring | Yes | 2025-06-01 |  | Not Started | DMT Project Manager | DRM Stormwater Delma-002-23 | KN
104 | Delma City | Um Alshuwaheen | 24.5036 | 52.3105 | Medium | No |  | Yes | Topography & Road Engineering | Need new network system | 2 |  |  | 600 | 1 | [9 empty] | 2500 | 0 | 0 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
105 | Delma City | Bad shayl | 24.4742 | 52.3164 | Medium | No |  | Yes | Inadequate design capacity | Need new network system | 4 |  |  | 1200 | 1 | [9 empty] | 2500 | 1 | 7000 | [10 empty] | Yes | Detailed Design | Stormwater Network including pipes, inlets and manholes | Permanent | no | 0 | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | N/A | N/A | 2025-06-01 | 2027-03-01 | Project Execution and Monitoring | Yes | 2025-06-01 |  | Not Started | DMT Project Manager | DRM Stormwater Delma-002-23 | KN
106 | Ghayathi City | الدوار الجنوبي | 23.8213 | 52.8111 | High | No |  | Yes | Inadequate design capacity | Need new network system | 6 |  |  | 1800 | 1 | [9 empty] | 2500 | 2 | 14000 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
107 | Ghayathi City | دوار القلعة | 23.8216 | 52.8179 | Medium | No |  | Yes | Inadequate design capacity | Need new network system | 4 |  |  | 1200 | 0 | [9 empty] | 0 | 2 | 14000 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
108 | Ghayathi City | دوار بدع المطاوعة | 23.829 | 52.8066 | Medium | No |  | Yes | Inadequate design capacity | Need new network system | 4 |  |  | 1200 | 0 | [9 empty] | 0 | 2 | 14000 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
109 | Ghayathi City | امام جمعية الظفرة | 23.8441 | 52.8085 | Medium | No |  | Yes | Inadequate design capacity | Need new network system | 4 |  |  | 1200 | 0 | [9 empty] | 0 | 2 | 14000 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
110 | Ghayathi City | دوار البلدية | 23.8455 | 52.809 | Medium | No |  | Yes | Inadequate design capacity | Need new network system | 4 |  |  | 1200 | 0 | [9 empty] | 0 | 2 | 14000 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
111 | Ghayathi City | دوار الدفاع | 23.8529 | 52.8083 | Medium | No |  | Yes | Inadequate design capacity | Need new network system | 4 |  |  | 1200 | 0 | [9 empty] | 0 | 2 | 14000 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
112 | Ghayathi City | طريق مبارك بن قران | 23.8696 | 52.8068 | Medium | No |  | Yes | Inadequate design capacity | Need new network system | 2 |  |  | 600 | 1 | [9 empty] | 2500 | 0 | 0 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
113 | Ghayathi City | مرابع غياثي | 23.9058 | 52.7926 | High | No |  | Yes | Inadequate design capacity | Need new network system | 4 |  |  | 1200 | 2 | [9 empty] | 5000 | 0 | 0 | [10 empty] | YES | Detailed Design | network with Pond outfall | Permenent | No | No | 1:5 & check 1:10 without flood | No | 44.88mm & check on 51.12mm | - | - | - | 2025-10-01 | 2027-06-22 | Under Construction | Yes | 2025-10-01 |  | On Track | DMT Project Manager |  | Al Torath / City Construction General Contracting
114 | Ghayathi City | مرابع غياثي | 23.9077 | 52.794 | High | No |  | Yes | Inadequate design capacity | Need new network system | 6 |  |  | 1800 | 2 | [9 empty] | 5000 | 1 | 7000 | [10 empty] | YES | Detailed Design | network with Pond outfall | Permenent | No | No | 1:5 & check 1:10 without flood | No | 44.88mm & check on 51.12mm | - | - | - | 2025-10-01 | 2027-06-22 | Under Construction | Yes | 2025-10-01 |  | On Track | DMT Project Manager |  | Al Torath / City Construction General Contracting
115 | Ghayathi City | مرابع غياثي | 23.9078 | 52.7954 | High | No |  | Yes | Inadequate design capacity | Need new network system | 4 |  |  | 1200 | 0 | [9 empty] | 0 | 2 | 14000 | [10 empty] | YES | Detailed Design | network with Pond outfall | Permenent | No | No | 1:5 & check 1:10 without flood | No | 44.88mm & check on 51.12mm | - | - | - | 2025-10-01 | 2027-06-22 | Under Construction | Yes | 2025-10-01 |  | On Track | DMT Project Manager |  | Al Torath / City Construction General Contracting
116 | Ghayathi City | مرابع غياثي | 23.9086 | 52.7925 | High | No |  | Yes | Inadequate design capacity | Need new network system | 4 |  |  | 1200 | 0 | [9 empty] | 0 | 2 | 14000 | [10 empty] | YES | Detailed Design | network with Pond outfall | Permenent | No | No | 1:5 & check 1:10 without flood | No | 44.88mm & check on 51.12mm | - | - | - | 2025-10-01 | 2027-06-22 | Under Construction | Yes | 2025-10-01 |  | On Track | DMT Project Manager |  | Al Torath / City Construction General Contracting
117 | Ghayathi City | مرابع غياثي | 23.9097 | 52.7926 | High | No |  | Yes | Inadequate design capacity | Need new network system | 4 |  |  | 1200 | 2 | [9 empty] | 5000 | 0 | 0 | [10 empty] | YES | Detailed Design | network with Pond outfall | Permenent | No | No | 1:5 & check 1:10 without flood | No | 44.88mm & check on 51.12mm | - | - | - | 2025-10-01 | 2027-06-22 | Under Construction | Yes | 2025-10-01 |  | On Track | DMT Project Manager |  | Al Torath / City Construction General Contracting
118 | Ghayathi City | مرابع غياثي | 23.9027 | 52.7978 | High | No |  | Yes | Inadequate design capacity | Need new network system | 2 |  |  | 600 | 0 | [9 empty] | 0 | 1 | 7000 | [10 empty] | YES | Detailed Design | network with Pond outfall | Permenent | No | No | 1:5 & check 1:10 without flood | No | 44.88mm & check on 51.12mm | - | - | - | 2025-10-01 | 2027-06-22 | Under Construction | Yes | 2025-10-01 |  | On Track | DMT Project Manager |  | Al Torath / City Construction General Contracting
119 | Ghayathi City | مرابع غياثي | 23.9049 | 52.8021 | High | No |  | Yes | Inadequate design capacity | Need new network system | 2 |  |  | 600 | 0 | [9 empty] | 0 | 1 | 7000 | [10 empty] | YES | Detailed Design | network with Pond outfall | Permenent | No | No | 1:5 & check 1:10 without flood | No | 44.88mm & check on 51.12mm | - | - | - | 2025-10-01 | 2027-06-22 | Under Construction | Yes | 2025-10-01 |  | On Track | DMT Project Manager |  | Al Torath / City Construction General Contracting
120 | Ghayathi City | مرابع غياثي | 23.908 | 52.7993 | High | No |  | Yes | Inadequate design capacity | Need new network system | 4 |  |  | 1200 | 2 | [9 empty] | 5000 | 0 | 0 | [10 empty] | YES | Detailed Design | network with Pond outfall | Permenent | No | No | 1:5 & check 1:10 without flood | No | 44.88mm & check on 51.12mm | - | - | - | 2025-10-01 | 2027-06-22 | Under Construction | Yes | 2025-10-01 |  | On Track | DMT Project Manager |  | Al Torath / City Construction General Contracting
121 | Ghayathi City | مرابع غياثي | 23.9046 | 52.8022 | High | No |  | Yes | Inadequate design capacity | Need new network system | 2 |  |  | 600 | 0 | [9 empty] | 0 | 1 | 7000 | [10 empty] | YES | Detailed Design | network with Pond outfall | Permenent | No | No | 1:5 & check 1:10 without flood | No | 44.88mm & check on 51.12mm | - | - | - | 2025-10-01 | 2027-06-22 | Under Construction | Yes | 2025-10-01 |  | On Track | DMT Project Manager |  | Al Torath / City Construction General Contracting
122 | Ghayathi City | مرابع غياثي | 23.9023 | 52.7996 | High | No |  | Yes | Inadequate design capacity | Need new network system | 2 |  |  | 600 | 0 | [9 empty] | 0 | 1 | 7000 | [10 empty] | YES | Detailed Design | network with Pond outfall | Permenent | No | No | 1:5 & check 1:10 without flood | No | 44.88mm & check on 51.12mm | - | - | - | 2025-10-01 | 2027-06-22 | Under Construction | Yes | 2025-10-01 |  | On Track | DMT Project Manager |  | Al Torath / City Construction General Contracting
123 | Ghayathi City | مرابع غياثي | 23.9135 | 52.7949 | High | No |  | Yes | Inadequate design capacity | Need new network system | 2 |  |  | 600 | 0 | [9 empty] | 0 | 1 | 7000 | [10 empty] | YES | Detailed Design | network with Pond outfall | Permenent | No | No | 1:5 & check 1:10 without flood | No | 44.88mm & check on 51.12mm | - | - | - | 2025-10-01 | 2027-06-22 | Under Construction | Yes | 2025-10-01 |  | On Track | DMT Project Manager |  | Al Torath / City Construction General Contracting
124 | Ghayathi City | شارع محمد بن حوفان المنصوري | 23.8843 | 52.7992 | Medium | No |  | Yes | Inadequate design capacity | Need new network system | 2 |  |  | 600 | 0 | [9 empty] | 0 | 1 | 7000 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
125 | Ghayathi City | شارع الروابط | 23.8823 | 52.8043 | Medium | No |  | Yes | Inadequate design capacity | Need new network system | 2 |  |  | 600 | 0 | [9 empty] | 0 | 1 | 7000 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
126 | Ghayathi City | شارع الروابط | 23.8806 | 52.8036 | High | No |  | Yes | Inadequate design capacity | Need new network system | 2 |  |  | 600 | 0 | [9 empty] | 0 | 1 | 7000 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
127 | Ghayathi City | مرابع غياثي | 23.917 | 52.7922 | High | No |  | Yes | Inadequate design capacity | Need new network system | 6 |  |  | 1800 | 2 | [9 empty] | 5000 | 1 | 7000 | [10 empty] | YES | Detailed Design | network with Pond outfall | Permenent | No | No | 1:5 & check 1:10 without flood | No | 44.88mm & check on 51.12mm | - | - | - | 2025-10-01 | 2027-06-22 | Under Construction | Yes | 2025-10-01 |  | On Track | DMT Project Manager |  | Al Torath / City Construction General Contracting
128 | Ghayathi City | مرابع غياثي | 23.9196 | 52.7957 | High | No |  | Yes | Inadequate design capacity | Need new network system | 2 |  |  | 600 | 0 | [9 empty] | 0 | 1 | 7000 | [10 empty] | YES | Detailed Design | network with Pond outfall | Permenent | No | No | 1:5 & check 1:10 without flood | No | 44.88mm & check on 51.12mm | - | - | - | 2025-10-01 | 2027-06-22 | Under Construction | Yes | 2025-10-01 |  | On Track | DMT Project Manager |  | Al Torath / City Construction General Contracting
129 | Ghayathi City | مرابع غياثي | 23.9125 | 52.802 | High | No |  | Yes | Inadequate design capacity | Need new network system | 2 |  |  | 600 | 0 | [9 empty] | 0 | 1 | 7000 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | N/A |  | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
130 | Ghayathi City | مرابع غياثي | 23.9022 | 52.7975 | High | No |  | Yes | Inadequate design capacity | Need new network system | 2 |  |  | 600 | 0 | [9 empty] | 0 | 1 | 7000 | [10 empty] | YES | Detailed Design | network with Pond outfall | Permenent | No | No | 1:5 & check 1:10 without flood | No | 44.88mm & check on 51.12mm | - | - | - | 2025-10-01 | 2027-06-22 | Under Construction | Yes | 2025-10-01 |  | On Track | DMT Project Manager |  | Al Torath / City Construction General Contracting
131 | Ghayathi City | شارع الروابط | 23.8806 | 52.8036 | Medium | No |  | Yes | Inadequate design capacity | Need new network system | 2 |  |  | 600 | 0 | [9 empty] | 0 | 1 | 7000 | [10 empty] | NO | Subject to the future Projects " same Point as Hot Spot 126" | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A |  |  | شارع الروابط " same Point as Hot Spot 126"
132 | Ghayathi City | شارع الروابط | 23.8345 | 52.8129 | Medium | No |  | Yes | Inadequate design capacity | Need new network system | 2 |  |  | 600 | 1 | [9 empty] | 2500 | 0 | 0 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
133 | Ghayathi City | الشعبية الجنوبية | 23.8256 | 52.8211 | Medium | No |  | Yes | Inadequate design capacity | Need new network system | 2 |  |  | 600 | 1 | [9 empty] | 2500 | 0 | 0 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
134 | Ghayathi City | الشعبية الجنوبية | 23.8271 | 52.8194 | Medium | No |  | Yes | Inadequate design capacity | Need new network system | 2 |  |  | 600 | 0 | [9 empty] | 0 | 1 | 7000 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
135 | Ghayathi City | شارع بستان العطاء | 23.8369 | 52.8093 | Medium | No |  | Yes | Inadequate design capacity | Need new network system | 4 |  |  | 1200 | 1 | [9 empty] | 2500 | 1 | 7000 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
136 | Liwa City | Sheikha Salama Bint Butti Roud | 23.1326 | 53.7966 | Very High | Yes |  | Yes | Inadequate design capacity | Need new network system | 2 |  |  | 600 | 0 | [9 empty] | 0 | 1 | 7000 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
137 | Liwa City | Sheikha Salama Bint Butti Roud | 23.1494 | 53.7945 | Very High | No |  | Yes | Inadequate design capacity | Need new network system | 4 |  |  | 1200 | 1 | [9 empty] | 2500 | 1 | 7000 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
138 | Liwa City | Al Timar Street | 23.1417 | 53.7903 | Medium | No |  | Yes | Inadequate design capacity | Need new network system | 4 |  |  | 1200 | 1 | [9 empty] | 2500 | 1 | 7000 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
139 | Liwa City | Sheikha Salama Bint Butti Roud | 23.1458 | 53.7798 | Medium | No |  | Yes | Inadequate design capacity | Need new network system | 2 |  |  | 600 | 0 | [9 empty] | 0 | 1 | 7000 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
140 | Liwa City | Sheikh Theyab Bin Eissa Al Falahi Road | 23.1337 | 53.7939 | Very High | No |  | Yes | Inadequate design capacity | Need new network system | 2 |  |  | 600 | 0 | [9 empty] | 0 | 1 | 7000 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
141 | Liwa City | Sheikha Salama Bint Butti Roud | 23.1378 | 53.7964 | Medium | No |  | Yes | Inadequate design capacity | Need new network system | 2 |  |  | 600 | 1 | [9 empty] | 2500 | 0 | 0 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
142 | Liwa City | Sheikh Theyab Bin Eissa Al Falahi Road | 23.1326 | 53.7747 | Low | No |  | Yes | Inadequate design capacity | Need new network system | 2 |  |  | 600 | 0 | [9 empty] | 0 | 1 | 7000 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
143 | Liwa City | Al Timar Street | 23.141 | 53.7895 | Medium | No |  | Yes | Inadequate design capacity | Need new network system | 2 |  |  | 600 | 0 | [9 empty] | 0 | 1 | 7000 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
144 | Liwa City | Abdallah Bin Ali Al Hameli Street | 23.1463 | 53.7971 | Medium | No |  | Yes | Inadequate design capacity | Need new network system | 2 |  |  | 600 | 1 | [9 empty] | 2500 | 0 | 0 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
145 | Liwa City | Sheikh Theyab Bin Eissa Al Falahi Road | 23.1184 | 53.7521 | High | No |  | Yes | Inadequate design capacity | Need new network system | 2 |  |  | 600 | 0 | [9 empty] | 0 | 1 | 7000 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
146 | Liwa City | Obid Bin Kenaish Ahameli Road | 23.1154 | 53.7589 | High | No |  | Yes | Inadequate design capacity | Need new network system | 4 |  |  | 1200 | 1 | [9 empty] | 2500 | 1 | 7000 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
147 | Liwa City | Sheikh Theyab Bin Eissa Al Falahi Road | 23.0868 | 53.6029 | High | No |  | Yes | Inadequate design capacity | Need new network system | 2 |  |  | 600 | 0 | [9 empty] | 0 | 1 | 7000 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
148 | Liwa City | Sheikh Theyab Bin Eissa Al Falahi Road | 23.1315 | 53.7586 | Low | No |  | Yes | Inadequate design capacity | Need new network system | 2 |  |  | 600 | 1 | [9 empty] | 2500 | 0 | 0 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
149 | Liwa City | Sheikh Theyab Bin Eissa Al Falahi Road | 23.1167 | 53.9433 | Medium | No |  | Yes | Inadequate design capacity | Need new network system | 2 |  |  | 600 | 0 | [9 empty] | 0 | 1 | 7000 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
150 | Liwa City | Sheikh Theyab Bin Eissa Al Falahi Road | 22.9877 | 54.219 | High | No |  | Yes | Inadequate design capacity | Need new network system | 4 |  |  | 1200 | 1 | [9 empty] | 2500 | 1 | 7000 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
151 | Liwa City | Obid Bin Kenaish Ahameli Road | 23.118 | 53.7546 | Medium | No |  | Yes | Inadequate design capacity | Need new network system | 2 |  |  | 600 | 1 | [9 empty] | 2500 | 0 | 0 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
152 | Liwa City | Sheikh Theyab Bin Eissa Al Falahi Road | 23.0741 | 54.0249 | Medium | No |  | Yes | Inadequate design capacity | Need new network system | 2 |  |  | 600 | 1 | [9 empty] | 2500 | 0 | 0 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
153 | Liwa City | Sheikh Theyab Bin Eissa Al Falahi Road | 23.0727 | 54.047 | High | No |  | Yes | Inadequate design capacity | Need new network system | 2 |  |  | 600 | 1 | [9 empty] | 2500 | 0 | 0 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
154 | Liwa City | Sheikh Theyab Bin Eissa Al Falahi Road | 22.9544 | 54.2423 | Medium | No |  | Yes | Inadequate design capacity | Need new network system | 4 |  |  | 1200 | 1 | [9 empty] | 2500 | 1 | 7000 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A
155 | Liwa City | Sheikh Theyab Bin Eissa Al Falahi Road | 23.1078 | 53.7268 | Low | No |  | Yes | Inadequate design capacity | Need new network system | 4 |  |  | 1200 | 1 | [9 empty] | 2500 | 1 | 7000 | [10 empty] | NO | Subject to the future Projects | N/A | Temporary subject to miscellaneous Project Approved Budget | TBC | TBC | N/A | N/A | 1 in 5 Years, check in 1 in 10 Years | 51.12 mm depth for 24hr | 0 | 0 | N/A | N/A | TBC subject to miscellaneous Project Approved Budget | N/A |  |  | Not Started | N/A

## Rate Assumptions
Average Rental Rates Assumptions
Resources | 12" Pump | 8" Pump | 6'' Pump | Labour | Tankers
Duty rate/Hr