## Instructions
Resilient Stormwater Network — 3-Line-of-Defense Sizing Model
Reverse-engineers pond capacity and mobile pump/tanker fleet size per hotspot, across 5/10/25/50/100-year storm scenarios.
How this model works
1. Hotspots sheet | Enter one row per drainage hotspot: catchment area, runoff coefficient, time of concentration, existing network capacity, and available pond capacity (0 if none exists yet). Score each hotspot 0-3 on five risk criteria — the model ranks hotspots automatically.
2. IDF_Dubai sheet | Reference rainfall Intensity-Duration-Frequency data, sourced from Dubai Municipality's Stormwater Design Guidelines (v2, July 2024), Table 0-2. Do not edit unless you have site-specific or updated IDF data (e.g. from Abu Dhabi ADM or your own gauge records).
3. Assumptions sheet | Global parameters used by every calculation — sedimentation allowance, hydrograph shape factor, drawdown time target, pump/tanker unit capacities. Yellow cells are meant to be reviewed and adjusted to your actual fleet and operational targets.
4. Scenario_Calc sheet | The engine. For every hotspot x return period combination, it pulls rainfall intensity, computes peak flow (Rational Method), compares it to existing network capacity, sizes the required pond volume, and — where ponds fall short — sizes the mobile pump and tanker response needed (Line 3).
5. Fleet_Summary sheet | Rolls the hotspot-level results up into total fleet requirements per storm scenario — this is what a control room would keep on standby for each severity level.
Colour legend
Blue text | Input cells — your data. Overwrite freely.
Yellow fill | Key assumptions — review before trusting the outputs; defaults are reasonable planning-level placeholders, not your fleet specs.
Black text | Formulas — do not overwrite; they reference the input/assumption cells.
Important limits — read before using this for real decisions
Screening tool, not final design | This uses the Rational Method and a simplified triangular-hydrograph approximation for pond volume. Dubai Municipality's own guidelines require InfoSWMM (or DM-approved equivalent) hydraulic/hydrograph modelling for actual pond and pumping-station sizing and DM approval. Use this model to prioritise hotspots and get planning-level orders of magnitude; commission a calibrated hydraulic model before committing capital.
Rational Method is capped | Per DM guidelines, the Rational Method is only valid for catchments under 80 hectares. Split larger catchments into sub-catchments, or use a hydrograph method.
Every hardcoded number is sourced | Check the Assumptions sheet and IDF_Dubai sheet notes for the source of every reference figure. Numbers marked ASSUMPTION are placeholders for you to replace with real fleet/operational data.

## Assumptions
Global Assumptions
Yellow = review and adjust. These drive every calculation in Scenario_Calc.
Parameter | Value | Source / basis
Sedimentation allowance factor | 1.05 | DM Stormwater Design Guidelines v2 (Jul 2024), Sec 5.1: ponds/off-line tanks sized 5% larger than the required attenuation volume to allow for sand/sediment deposition.
Hydrograph shape / attenuation factor | 0.5 | ASSUMPTION - simplified triangular-hydrograph approximation of excess-flow volume (0.5 x peak excess flow x duration). Replace with actual SWMM/InfoSWMM routing output before final design; DM Sec 5.8 mandates InfoSWMM (or DM-approved equivalent) for real drainage system modelling.
Target hotspot drawdown / response time (hr) | 2 | ASSUMPTION - the time within which Line 3 (mobile pumps/tankers) should clear the pond shortfall at a hotspot once dispatched. Set to your own operational SLA.
Mobile pump unit capacity (m3/hr) | 300 | ASSUMPTION - typical large trailer-mounted diesel pump (150-200mm bore) throughput. Replace with your actual fleet's rated capacity.
Tanker capacity (m3 per load) | 15 | ASSUMPTION - typical vacuum tanker load size. Replace with your actual fleet's tanker capacity.
Runoff Coefficient Adjustment Factors (Cf)
Source: DM Stormwater Design Guidelines v2, Table 0-6 (after TxDOT, 2011). Applied because infiltration/losses matter proportionally less in higher-return-period storms. C x Cf capped at 1.0 in Scenario_Calc.
Return Period (yr) | Cf
5 | 1
10 | 1
25 | 1.1
50 | 1.2
100 | 1.25

## IDF_Dubai
Dubai Rainfall Intensity-Duration-Frequency (IDF) Table
Source: Dubai Municipality, Stormwater Design Guidelines, Doc. DM-WSA-SRPD-SW1, Version 2, July 2024, Table 0-2 ("IDF values for Dubai including the Estimated values"). Intensities in mm/hr.
For sites in the Hatta area, use Table 0-3 of the same document instead (materially higher intensities) - not reproduced here.
Return Period (yr) \ Duration (min) | 5 | 10 | 15 | 20 | 30 | 45 | 60 | 90 | 120 | 180 | 240 | 300 | 360 | 720 | 1440
2 | 59.9 | 45.22 | 37.15 | 31.1 | 23.57 | 17.44 | 13.87 | 10.22 | 8.18 | 5.92 | 4.73 | 3.96 | 3.38 | 1.93 | 1
5 | 97.41 | 76.98 | 63.34 | 53.54 | 41.68 | 31.78 | 25.35 | 18.66 | 15.11 | 10.81 | 8.62 | 7.21 | 6.22 | 3.68 | 1.93
10 | 118 | 97.61 | 80.41 | 68.58 | 54.72 | 42.82 | 34.22 | 25.18 | 20.57 | 14.6 | 11.61 | 9.73 | 8.44 | 5.13 | 2.71
20 | 131.23 | 115.25 | 95.09 | 82.01 | 67.36 | 54.26 | 43.46 | 31.95 | 26.37 | 18.54 | 14.7 | 12.34 | 10.79 | 6.75 | 3.59
25 | 133.66 | 120.18 | 99.22 | 85.92 | 71.32 | 58.03 | 46.52 | 34.2 | 28.31 | 19.84 | 15.72 | 13.2 | 11.58 | 7.31 | 3.9
50 | 169.22 | 152.15 | 125.61 | 108.78 | 90.3 | 73.47 | 58.89 | 43.29 | 35.85 | 25.12 | 19.91 | 16.71 | 14.65 | 9.25 | 4.94
100 | 209.2 | 188.11 | 155.29 | 134.49 | 111.63 | 90.83 | 72.81 | 53.52 | 44.32 | 31.06 | 24.61 | 20.66 | 18.12 | 11.44 | 6.1

## Hotspots
Hotspot Register
One row per hotspot. Orange rows are EXAMPLES - replace with your own sites. Risk scores are 0 (none) to 3 (severe); Risk Score and Rank are calculated.
Hotspot ID | Location / Description | Catchment Area (ha) | Runoff Coeff C (0-1) | Time of Concentration tc (min) | Network Design Return Period (yr) | Existing Network Capacity Qcap (m3/s) | Available Pond Capacity (m3) | Elevation / Low-point Risk (0-3) | Historical Flooding Risk (0-3) | Distance-to- Outfall Risk (0-3) | Critical Asset Proximity Risk (0-3) | Imperviousness Risk (0-3) | Risk Score | Risk Rank
H1 | EXAMPLE - Underpass at main arterial / low-lying junction | 12 | 0.75 | 20 | 10 | 1.8 | 0 | 3 | 3 | 1 | 3 | 3 | 13 | 1
H2 | EXAMPLE - Residential low point, far from outfall | 35 | 0.45 | 45 | 5 | 2.6 | 4500 | 3 | 2 | 3 | 0 | 1 | 9 | 3
H3 | EXAMPLE - Commercial/downtown catchment near coastline | 22 | 0.85 | 25 | 10 | 3.1 | 8000 | 1 | 1 | 0 | 1 | 3 | 6 | 5
H4 | EXAMPLE - New residential district, sandy soil, gentle slope | 60 | 0.35 | 60 | 5 | 3.4 | 0 | 1 | 0 | 1 | 0 | 0 | 2 | 6
H5 | EXAMPLE - Airport-adjacent culvert catchment | 40 | 0.6 | 30 | 25 | 4 | 6000 | 2 | 1 | 1 | 3 | 2 | 9 | 3
H6 | EXAMPLE - Government building precinct, basement car parks | 8 | 0.8 | 15 | 10 | 1.2 | 2000 | 2 | 2 | 2 | 3 | 2 | 11 | 2

## Scenario_Calc
Scenario Calculator - Pond Volume & Mobile Fleet Sizing per Hotspot x Return Period
Enter each Hotspot ID against each Return Period you want to test (5/10/25/50/100 yr - matching IDF_Dubai rows). All other columns are formulas pulling from Hotspots, IDF_Dubai, and Assumptions.
Hotspot ID | Return Period (yr) | Hotspot Name | tc (min) | Duration Bucket Used (min) | Rainfall Intensity I (mm/hr) | Catchment Area A (ha) | Base Runoff Coeff C | Cf Factor | Adjusted C (C x Cf, capped 1) | Peak Flow Q (m3/s) | Existing Network Capacity Qcap (m3/s) | Excess Flow (m3/s) | Storm Duration (sec) | Hydrograph Shape Factor | Flood Volume (m3) | Sedimentation Factor | Required Pond Volume (m3) | Available Pond Capacity (m3) | Pond Shortfall (m3) | Drawdown Time (hr) | Residual Flow Rate Needed (m3/hr) | Pump Unit Capacity (m3/hr) | Mobile Pumps Required | Tanker Capacity (m3) | Tanker Loads Required
H1 | 5 | EXAMPLE - Underpass at main arterial / low-lying junction | 20 | 20 | 53.54 | 12 | 0.75 | 1 | 0.75 | 1.3385 | 1.8 | 0 | 1200 | 0.5 | 0 | 1.05 | 0 | 0 | 0 | 2 | 0 | 300 | 0 | 15 | 0
H1 | 10 | EXAMPLE - Underpass at main arterial / low-lying junction | 20 | 20 | 68.58 | 12 | 0.75 | 1 | 0.75 | 1.7145 | 1.8 | 0 | 1200 | 0.5 | 0 | 1.05 | 0 | 0 | 0 | 2 | 0 | 300 | 0 | 15 | 0
H1 | 25 | EXAMPLE - Underpass at main arterial / low-lying junction | 20 | 20 | 85.92 | 12 | 0.75 | 1.1 | 0.825 | 2.3628 | 1.8 | 0.5628 | 1200 | 0.5 | 337.68 | 1.05 | 354.564 | 0 | 354.564 | 2 | 177.282 | 300 | 1 | 15 | 24
H1 | 50 | EXAMPLE - Underpass at main arterial / low-lying junction | 20 | 20 | 108.78 | 12 | 0.75 | 1.2 | 0.9 | 3.2634 | 1.8 | 1.4634 | 1200 | 0.5 | 878.04 | 1.05 | 921.942 | 0 | 921.942 | 2 | 460.971 | 300 | 2 | 15 | 62
H1 | 100 | EXAMPLE - Underpass at main arterial / low-lying junction | 20 | 20 | 134.49 | 12 | 0.75 | 1.25 | 0.9375 | 4.2028 | 1.8 | 2.4028 | 1200 | 0.5 | 1441.6875 | 1.05 | 1513.7719 | 0 | 1513.7719 | 2 | 756.8859 | 300 | 3 | 15 | 101
H2 | 5 | EXAMPLE - Residential low point, far from outfall | 45 | 45 | 31.78 | 35 | 0.45 | 1 | 0.45 | 1.3904 | 2.6 | 0 | 2700 | 0.5 | 0 | 1.05 | 0 | 4500 | 0 | 2 | 0 | 300 | 0 | 15 | 0
H2 | 10 | EXAMPLE - Residential low point, far from outfall | 45 | 45 | 42.82 | 35 | 0.45 | 1 | 0.45 | 1.8734 | 2.6 | 0 | 2700 | 0.5 | 0 | 1.05 | 0 | 4500 | 0 | 2 | 0 | 300 | 0 | 15 | 0
H2 | 25 | EXAMPLE - Residential low point, far from outfall | 45 | 45 | 58.03 | 35 | 0.45 | 1.1 | 0.495 | 2.7927 | 2.6 | 0.19269 | 2700 | 0.5 | 260.1366 | 1.05 | 273.1434 | 4500 | 0 | 2 | 0 | 300 | 0 | 15 | 0
H2 | 50 | EXAMPLE - Residential low point, far from outfall | 45 | 45 | 73.47 | 35 | 0.45 | 1.2 | 0.54 | 3.8572 | 2.6 | 1.2572 | 2700 | 0.5 | 1697.1863 | 1.05 | 1782.0456 | 4500 | 0 | 2 | 0 | 300 | 0 | 15 | 0
H2 | 100 | EXAMPLE - Residential low point, far from outfall | 45 | 45 | 90.83 | 35 | 0.45 | 1.25 | 0.5625 | 4.9673 | 2.6 | 2.3673 | 2700 | 0.5 | 3195.8086 | 1.05 | 3355.599 | 4500 | 0 | 2 | 0 | 300 | 0 | 15 | 0
H3 | 5 | EXAMPLE - Commercial/downtown catchment near coastline | 25 | 20 | 53.54 | 22 | 0.85 | 1 | 0.85 | 2.7811 | 3.1 | 0 | 1200 | 0.5 | 0 | 1.05 | 0 | 8000 | 0 | 2 | 0 | 300 | 0 | 15 | 0
H3 | 10 | EXAMPLE - Commercial/downtown catchment near coastline | 25 | 20 | 68.58 | 22 | 0.85 | 1 | 0.85 | 3.5623 | 3.1 | 0.46235 | 1200 | 0.5 | 277.41 | 1.05 | 291.2805 | 8000 | 0 | 2 | 0 | 300 | 0 | 15 | 0
H3 | 25 | EXAMPLE - Commercial/downtown catchment near coastline | 25 | 20 | 85.92 | 22 | 0.85 | 1.1 | 0.935 | 4.9094 | 3.1 | 1.8094 | 1200 | 0.5 | 1085.624 | 1.05 | 1139.9052 | 8000 | 0 | 2 | 0 | 300 | 0 | 15 | 0
H3 | 50 | EXAMPLE - Commercial/downtown catchment near coastline | 25 | 20 | 108.78 | 22 | 0.85 | 1.2 | 1 | 6.6477 | 3.1 | 3.5477 | 1200 | 0.5 | 2128.6 | 1.05 | 2235.03 | 8000 | 0 | 2 | 0 | 300 | 0 | 15 | 0
H3 | 100 | EXAMPLE - Commercial/downtown catchment near coastline | 25 | 20 | 134.49 | 22 | 0.85 | 1.25 | 1 | 8.2188 | 3.1 | 5.1188 | 1200 | 0.5 | 3071.3 | 1.05 | 3224.865 | 8000 | 0 | 2 | 0 | 300 | 0 | 15 | 0
H4 | 5 | EXAMPLE - New residential district, sandy soil, gentle slope | 60 | 60 | 25.35 | 60 | 0.35 | 1 | 0.35 | 1.4788 | 3.4 | 0 | 3600 | 0.5 | 0 | 1.05 | 0 | 0 | 0 | 2 | 0 | 300 | 0 | 15 | 0
H4 | 10 | EXAMPLE - New residential district, sandy soil, gentle slope | 60 | 60 | 34.22 | 60 | 0.35 | 1 | 0.35 | 1.9962 | 3.4 | 0 | 3600 | 0.5 | 0 | 1.05 | 0 | 0 | 0 | 2 | 0 | 300 | 0 | 15 | 0
H4 | 25 | EXAMPLE - New residential district, sandy soil, gentle slope | 60 | 60 | 46.52 | 60 | 0.35 | 1.1 | 0.385 | 2.985 | 3.4 | 0 | 3600 | 0.5 | 0 | 1.05 | 0 | 0 | 0 | 2 | 0 | 300 | 0 | 15 | 0
H4 | 50 | EXAMPLE - New residential district, sandy soil, gentle slope | 60 | 60 | 58.89 | 60 | 0.35 | 1.2 | 0.42 | 4.1223 | 3.4 | 0.7223 | 3600 | 0.5 | 1300.14 | 1.05 | 1365.147 | 0 | 1365.147 | 2 | 682.5735 | 300 | 3 | 15 | 92
H4 | 100 | EXAMPLE - New residential district, sandy soil, gentle slope | 60 | 60 | 72.81 | 60 | 0.35 | 1.25 | 0.4375 | 5.3091 | 3.4 | 1.9091 | 3600 | 0.5 | 3436.3125 | 1.05 | 3608.1281 | 0 | 3608.1281 | 2 | 1804.0641 | 300 | 7 | 15 | 241
H5 | 5 | EXAMPLE - Airport-adjacent culvert catchment | 30 | 30 | 41.68 | 40 | 0.6 | 1 | 0.6 | 2.7787 | 4 | 0 | 1800 | 0.5 | 0 | 1.05 | 0 | 6000 | 0 | 2 | 0 | 300 | 0 | 15 | 0
H5 | 10 | EXAMPLE - Airport-adjacent culvert catchment | 30 | 30 | 54.72 | 40 | 0.6 | 1 | 0.6 | 3.648 | 4 | 0 | 1800 | 0.5 | 0 | 1.05 | 0 | 6000 | 0 | 2 | 0 | 300 | 0 | 15 | 0
H5 | 25 | EXAMPLE - Airport-adjacent culvert catchment | 30 | 30 | 71.32 | 40 | 0.6 | 1.1 | 0.66 | 5.2301 | 4 | 1.2301 | 1800 | 0.5 | 1107.12 | 1.05 | 1162.476 | 6000 | 0 | 2 | 0 | 300 | 0 | 15 | 0
H5 | 50 | EXAMPLE - Airport-adjacent culvert catchment | 30 | 30 | 90.3 | 40 | 0.6 | 1.2 | 0.72 | 7.224 | 4 | 3.224 | 1800 | 0.5 | 2901.6 | 1.05 | 3046.68 | 6000 | 0 | 2 | 0 | 300 | 0 | 15 | 0
H5 | 100 | EXAMPLE - Airport-adjacent culvert catchment | 30 | 30 | 111.63 | 40 | 0.6 | 1.25 | 0.75 | 9.3025 | 4 | 5.3025 | 1800 | 0.5 | 4772.25 | 1.05 | 5010.8625 | 6000 | 0 | 2 | 0 | 300 | 0 | 15 | 0
H6 | 5 | EXAMPLE - Government building precinct, basement car parks | 15 | 15 | 63.34 | 8 | 0.8 | 1 | 0.8 | 1.126 | 1.2 | 0 | 900 | 0.5 | 0 | 1.05 | 0 | 2000 | 0 | 2 | 0 | 300 | 0 | 15 | 0
H6 | 10 | EXAMPLE - Government building precinct, basement car parks | 15 | 15 | 80.41 | 8 | 0.8 | 1 | 0.8 | 1.4295 | 1.2 | 0.22951 | 900 | 0.5 | 103.28 | 1.05 | 108.444 | 2000 | 0 | 2 | 0 | 300 | 0 | 15 | 0
H6 | 25 | EXAMPLE - Government building precinct, basement car parks | 15 | 15 | 99.22 | 8 | 0.8 | 1.1 | 0.88 | 1.9403 | 1.2 | 0.7403 | 900 | 0.5 | 333.136 | 1.05 | 349.7928 | 2000 | 0 | 2 | 0 | 300 | 0 | 15 | 0
H6 | 50 | EXAMPLE - Government building precinct, basement car parks | 15 | 15 | 125.61 | 8 | 0.8 | 1.2 | 0.96 | 2.6797 | 1.2 | 1.4797 | 900 | 0.5 | 665.856 | 1.05 | 699.1488 | 2000 | 0 | 2 | 0 | 300 | 0 | 15 | 0
H6 | 100 | EXAMPLE - Government building precinct, basement car parks | 15 | 15 | 155.29 | 8 | 0.8 | 1.25 | 1 | 3.4509 | 1.2 | 2.2509 | 900 | 0.5 | 1012.9 | 1.05 | 1063.545 | 2000 | 0 | 2 | 0 | 300 | 0 | 15 | 0

## Fleet_Summary
Control-Room Fleet Summary - Total Readiness Required per Storm Scenario
Sums Scenario_Calc across all hotspots for each return period - i.e. what the central command/control room should have staged and ready for a storm of that severity across the whole network.
Return Period (yr) | Total Peak Flow Demand (m3/s) | Total Excess Flow (m3/s) | Total Required Pond Volume (m3) | Total Available Pond Volume (m3) | Total Pond Shortfall (m3) | Total Mobile Pumps Required | Total Tanker Loads Required
5 | 10.8934 | 0 | 0 | 20500 | 0 | 0 | 0
10 | 14.2239 | 0.69186 | 399.7245 | 20500 | 0 | 0 | 0
25 | 20.2203 | 4.5353 | 3279.8814 | 20500 | 354.564 | 1 | 24
50 | 27.7942 | 11.6942 | 10049.9934 | 20500 | 2287.089 | 5 | 154
100 | 35.4514 | 19.3514 | 17776.7715 | 20500 | 5121.9 | 10 | 342
Read this as: at a 1-in-100yr event, this is the total number of mobile pumps and tanker loads the control room should be able to mobilise network-wide, on top of whatever the existing network and ponds already absorb.